## Slide 1: Traditional Advanced Control Strategies
High level application of PID controller
  Time delay Compensator
  Cascade Control
  Split range Control
  Selective control
  Override Control
  Valve Position Control
  Variable Structure Control
Feedforward and Ratio Control

## Slide 2: Feedforward & Ratio Control

## Slide 3: Feedback Control
Advantages of Feedback Control
Corrective action occurs as soon as the controlled variable deviates from the set point, regardless of the source and type of disturbance.
Feedback control requires minimal knowledge about the process to be controlled; in particular, a mathematical model of the process is not required, although it can be very useful for control system design.
PID controller is both versatile and robust. If process conditions change, retuning the controller usually produces satisfactory control.

## Slide 4: Feedback Control
Disadvantages of Feedback Control
Corrective action is taken only after a deviation in the controlled variable occurs. Thus, perfect control, where the controlled variable does not deviate from the set point during disturbance or set-point changes, is theoretically impossible.
Feedback control does not provide predictive control action to compensate for the effects of known or measurable disturbances.
It may not be satisfactory for processes with large time constants and/or long time delays. If large and frequent disturbances occur, the process may operate continuously in a transient state and never attain the desired steady state.
In some situations, the controlled variable cannot be measured on-line, and, consequently, feedback control is not feasible.

## Slide 5: FeedForward Control
The basic concept of feedforward control is to measure important disturbance variables and take corrective action before they upset the process.
Rapid disturbance changes can occur as a result of steam demands made by downstream processing units.
This control system tends to be quite sensitive to rapid changes in the disturbance variable, steam flow rate, as a result of the small liquid capacity of the boiler drum.

## Slide 6: Feedforward Control
The feedforward control scheme can provide better control of the liquid level. Here the steam flow rate is measured, and the feedforward controller adjusts the feed water flow rate.

## Slide 7: Feedforward-Feedback Control
In practical applications, feedforward control is normally used in combination with feedback control.
Feedforward control is used to reduce the effects of measurable disturbances, while feedback trim compensates for inaccuracies in the process model, measurement error, and unmeasured disturbances.

## Slide 8: Derivation of FF Controller

## Slide 9: Lead/Lag Element for Implementing FF Control

## Slide 10: Feedforward Control
SSFF  SSFFD 
FFwD 
FF =

## Slide 11: Feedforward Control
Points to consider:
If , then
So the feedforward control element is not practically realizable because of predictive element.
However, we can approximate it by omitting the term and increasing the value of the lead time constant from to .
If then , it is physically unrealizable. Here, also we can approximate as

## Slide 12: Combined FF and FB Control
feedback trim compensates for inaccuracies in the process model, measurement error, and unmeasured disturbances.
Stability of the feedback loop is not altered by the Feedforward Controller

## Slide 13: Combined FF and FB Control

## Slide 14: Ratio Control
Ratio control is a special type of feedforward control that has had widespread application in the process industries.
The objective is to maintain the ratio of two process variables as a specified value.
The two variables are usually flow rates, a manipulated variable u, and a disturbance variable d.
Thus, the ratio is controlled rather than the individual variables.

## Slide 15: Typical applications of ratio control
Setting the relative amounts of components in blending operations
Advantage
Actual ratio R is calculated.
Disadvantage
Divider element must be included in the loop, and this element makes the process gain vary in a nonlinear fashion.

## Slide 16: Typical applications of ratio control
Preferred Scheme of Ratio Control.
Regardless of how ratio control is implemented, the process variables must be scaled appropriately.
Gain setting for the ratio station Kr must take into account the spans of the two flow transmitters.

## Slide 17: Typical applications of ratio control
Maintaining a stoichiometric ratio of reactants to a reactor
0-30 l/m
0-15 l/m
Gain = ?

## Slide 18: Ratio Control for Wastewater Neutralization
The output of the pH controller is the ratio of NaOH flow rate to acid wastewater flow rate; therefore, the product of the controller output and the measured acid wastewater flow rate become the setpoint for the flow controller of the NaOH addition.

## Slide 19: Ratio Control Requiring Dynamic Compensation

## Slide 20: Override/Select Controls
Process are many times operated at the safety or equipment limits in order to maximize process throughput.
During upset periods, it is essential that safety limits are enforced.
Objective:
Regulate level and exit flow rate of sand water slurry
Slurry velocity in the exit line must be above lower limit
Normal : LC is operating
Too Low Flow: FC overtakes

## Slide 21: Furnace Tube Temperature Constraint Control
Under normal operation, the controller adjusts the furnace firing rate to maintain process stream at the setpoint temperature.
At higher fuel rates, excessive tube temperatures can result greatly reducing the useful life of the furnace tubes.
The LS controller reduces the firing rate to ensure that the furnace tubes are not damaged.

## Slide 22: Column Flooding Constraint Control
Objectives:
Maintain the temperature at set point (composition control)
Maintain P < Pmax (preventing flooding)
Normal: temperature controller is working
If P is too high, the differential pressure (DP) controller takes over and reduce the steam flow set point.
Temp. controller: PI controller
DP controller: tightly tuned
P control with flooding limit of DP

## Slide 23: Controlling Multiple Constraints

## Slide 24: Cross-Limiting Firing Controls
It is critical that excess oxygen is maintained during firing rate increases or decreases or CO will form.

## Slide 25: Cross-Limiting Firing Controls
It is critical that excess oxygen is maintained during firing rate increases or decreases or CO will form.
When the firing rate is increased, the air flow rate will lead the fuel flow rate.

## Slide 26: Cross-Limiting Firing Controls
It is critical that excess oxygen is maintained during firing rate increases or decreases or CO will form.
When the firing rate is decreased, the fuel flow rate will lead the air flow rate.

## Slide 27: Valve Position Control
Objectives:
• Supply energy to downstream processes as they require
• Minimize the energy consumption of heater
Heater outlet controller:
maintain the temp of the heater as it directed for enough supply of energy to down stream processes
Valve position controller:
• Adjust the TC set point
so that the valve opening
of at least one of the valves
is near “fully open”.
(slow control)
• I-control can be used.
(slow but no offset)
• The SP should be around
90-95% (fully open).

## Slide 28: Mixing Tank Cooling Control
Objectives:
• Remove the heat of mixing and maintain mixture temperature
• Maximize the production of mixed feed
Cascaded jacketed tank temp controller: maintain the temp of the mixture by removal of heat of mixing using cooling water
Valve position controller:
• Increase the feed flow of A while cooling capacity allows. (slow control)
• Mix ratio is maintained by
ratio control scheme
• The SP should be around
90-95% (fully open).

## Slide 29: Floating pressure of distillation column
Objectives:
Maintain the column pressure by adjusting reflux flow rate
If the level is too low (below the heat transfer area), the vent must be open to relieve the column pressure.
Pressure Controller: control the P by adjusting reflux flow rate.
Level controller: takes over if level is too low. (L<Lmin)
If LC takes over, there is a discrepancy, and it opens the vent valve.
The K in summing station decides the vent opening.

## Slide 30: Blending Process Control
Objectives:
Maintain product composition
Maximize production
The additive flow rates are limited (constrained)
Control scheme:
Override control for max production
Ratio control for composition
Valve position control for additive flow constraint