## Slide 1: Review of Feedback Control System

## Slide 2: Transfer Function for a PID Controller
Ideal PID :
Real PID :
Derivative Kick:
To avoid sudden jump of output due to setpoint change, sensor output is used in place of error term, i.e,

## Slide 3: Direct / Reverse acting controller
What will be the sign of the controller gain?

## Slide 4: Guidelines for Selecting Direct and Reverse Acting PID’s
Consider a direct acting final control element to be positive and reverse to be negative.
If the sign of the product of the final control element and the process gain is positive, use the reverse acting PID algorithm.
If the sign of the product is negative, use the direct acting PID algorithm
If control signal goes to a control valve with a valve positioner, the actuator is considered direct acting.

## Slide 5
Level Control Example
Process gain is positive because when flow in is increased, the level increases.
If the final control element is direct acting, use reverse acting PID.
For reverse acting final control element, use direct acting PID.

## Slide 6: Level Control Example
Process gain is negative because when flow out is increased, the level decreases.
If the final control element is direct acting, use direct acting PID.
For reverse acting final control element, use reverse acting PID.

## Slide 7: General Feedback Control Loop
GP(s)
Ga(s)
GC(s)
KS
GS(s)
Gd(s)
d(s)
ysp(s)
+
-
+
+
u(s)
y(s)
c(s)
e(s)
yS(s)
Characteristic Polynomial : 1 + GOL = 0 or

## Slide 8: Controller actions on feedback dynamics
Process G(s) : Controller : Proportional, ;
Matlab:
s=tf(‘s’); g=1/(s+1)^3;
step(g); hold on
for kc=[0.5:0.5:2],
gcl=feedback(kc*g,1);
step(gcl);
end

## Slide 9: Proportional Control
Important points:
  proportional feedback does not change the order of the system
    started with a first order process
    closed-loop process also first order
    order of characteristic polynomial is invariant under proportional feedback
  speed of response of closed-loop process is directly affected by controller gain
    increasing controller gain reduces the closed-loop time constant
  In general, proportional feedback
    reduces (does not eliminate) offset
    speeds up response
    for oscillatory processes, makes closed-loop process more oscillatory

## Slide 10: Controller actions on feedback dynamics
Process G(s) : Controller : PI (I varying) ;
Matlab:
figure; hold on; kc=2;
for Ti=[2:1:5],
gc=tf(kc*[1,1/Ti],[1,0]);
gcl=feedback(gc*g,1);
step(gcl);
end

## Slide 11: Proporional - Integral Control
Important points:
  integral action increases order of the system in closed-loop
  integral action eliminates offset
  integral action
    should be small compared to proportional action
    tuned to slowly eliminate offset
    can increase or cause oscillation
    can be de-stabilizing
  PI controller has two tuning parameters that can independently affect
    speed of response
    Nature of response (oscillation)
  PI is the most widely used controller in industry
    optimal structure for first order processes

## Slide 12: Controller actions on feedback dynamics
Process G(s) : Controller : PD, ;
Matlab:
figure; hold on; kc=2;
for Td=[0:0.2:0.8],
gc=tf(kc*[Td,1],[1]);
gcl=feedback(gc*g,1);
step(gcl); end

## Slide 13: Proportional Derivative
Important Points:
  derivative action does not increase the order of the system
  Used to compensate for trends in output
    measure of speed of error signal change
    provides predictive or anticipatory action
  adding derivative action affects the period of oscillation of the process
    good for disturbance rejection
    poor for tracking
  derivative action
    should be small compared to integral action
    has a stabilizing influence
    difficult to use for noisy signals
    usually modified in practical implementation

## Slide 14: PID control (Setpoint Tracking or Servo Control)

## Slide 15: Disturbance Rejection: Input dynamics

## Slide 16: Closed-loop Stability
Every control problem involves a consideration of closed-loop stability
General concepts:
BIBO Stability:
  “ An (unconstrained) linear system is said to be stable if the output response is bounded for all bounded inputs. Otherwise it is unstable.”
  Comments:
    Stability is much easier to prove than instability
    This is just one type of stability

## Slide 17: Closed-loop Stability
General Stability criterion:
  “ A closed-loop feedback control system is stable if and only if all roots of the characteristic polynomial (1+ GOL=0) are negative or have negative real parts. Otherwise, the system is unstable.”
  Unstable region is the right half plane of the complex plane.
  Valid for any linear systems.
  Underlying system is almost always nonlinear so stability holds only locally. Moving away from the point of linearization may cause instability

## Slide 18: Stability Analysis Methods
Problem reduces to finding roots of a polynomial
Traditional:
  1. Routh array:
    Test for positivity of roots of a polynomial
  2. Direct substitution
    Complex axis separates stable and unstable regions
    Find controller gain that yields purely complex roots
  3. Root locus diagram
    Vary location of poles as controller gain is varied
    Of limited use
  Bode stability criteria
  Niquist Stability criteria

## Slide 19: Closed-loop stability
Routh array for a polynomial equation
is
where
Elements of left column must be positive to have roots with negative real parts

## Slide 20: Example: Routh Array
Characteristic polynomial
Polynomial Coefficients
Routh Array
  Closed-loop system is unstable
1
2
3
4
5
6

## Slide 21: Direct Substitution
Technique to find gain value that de-stabilizes the system.
Observation:
  Process becomes unstable when poles appear on right half plane
Find value of Kc that yields purely complex poles
Strategy:
  Start with characteristic polynomial
  Write characteristic equation:
  Substitute for complex pole (s=jw)
  Solve for Kc and w

## Slide 22: Example: Direct Substitution
Characteristic equation
Substitution for s=jw
Real Part : Complex Part:
  System is unstable if

## Slide 23: Root Locus Diagram
Old method that consists in plotting roots of characteristic polynomial (closed loop poles) as controller gain is changed.
Matlab
s=tf(‘s’);
G1=1/(s+1);
G2=1/(s+2);
G3=1/(s+3);
G=G1*G2*G3;
rlocus(G);
rlocfind(G);

## Slide 24: Frequency Response
Process
t
Amplitude Ratio (AR) = Â/A
Phase lag ( = -t/P*180
The process acts as a “filter” or “amplifier” that attenuates or amplifies the input at frequency .
The frequency response of a process G(s) at a specific frequency is a complex number and can be obtained by substituting
P

## Slide 25: Frequency Response
Two ways of representing the frequency response
  Bode Plot
    Log-Log plot of AR vs and semi-log plot vs
  Nyquist Plot
    Plot of Re() vs Im() for various values of .
    Frequency does not appear explicitly in this plot.

## Slide 26: Bode Plot
Meeting pt of LFA and HFA
Steady state gain:
Bandwidth, , defines the highest frequency at which the process displays no attenuation. It is calculated based on the frequency when amplitude reaches 0.707 K.
Roll-off is slope of decaying AR at high frequencies.

## Slide 27
Crossover
AR(

## Slide 28: Bode Stability Criterion
Consider open-loop control system
1. Introduce sinusoidal input in setpoint (D(s)=0) and observe sinusoidal output
2. Fix gain such AR=1 and input frequency such that =-180
3. At same time, connect close the loop and set YSP(s)=0
Q: What happens if AR <1, 1 and >1?
Open-loop Response to YSP(s)
Gp
Gc
Gs
D(s)
Y(s)
Ys(s)
YSP(s)
U(s)
+
-
+
+

## Slide 29: Bode Stability Criterion
A closed-loop system is unstable if the frequency of the response of the open-loop GOL has an amplitude ratio greater than one at the critical frequency. Otherwise it is stable.
Strategy:
1. Solve for w in
2. Calculate AR

## Slide 30: Bode Stability Criterion
To check for stability:
1. Compute open-loop transfer function
2. Solve for w in f=-p
3. Evaluate AR at w
4. If AR>1 then process is unstable
Find ultimate gain:
1. Compute open-loop transfer function without controller gain
2. Solve for w in f=-p
3. Evaluate AR at w
4. Let

## Slide 31: Bode Criterion
Consider the transfer function and controller
- Open-loop transfer function
- Amplitude ratio and phase shift
- At f=-p, w=1.4128, AR=6.746

## Slide 32: Bode Stability
Phase Crossover frequency (is the frequency at which phase lag is 1800.
Gain Crossover frequency () is the frequency at which AR = 1
Gain Margin (GM) is the amount of gain required for the AR to reach 1 at phase crossover frequency.
  GM=1/ARC , where ARC is the Amplitude ratio at gain crossover frequency.
Phase Margin (PM) is the amount of phase difference required for phase lag to reach 1800 at gain crossover frequency. PM=180+ where is phase lag at phase crossover frequency.

## Slide 33: Gain Margin and Phase Margin
dB=20 log10AR
Wcg is the frequency where the gain margin is measured, which is a -180° phase crossing frequency.
Wcp is the frequency where the phase margin is measured, which is a 0-dB gain crossing frequency.

## Slide 34: Nyquist Stability Criterion
If N is the number of times that the Nyquist plot encircles the point (-1,0) in the complex plane in the clockwise direction, and P is the number of open-loop poles of GOL that lie in the right-half plane, then Z=N+P is the number of unstable roots of the closed-loop characteristic equation.
Strategy
1. Substitute s=jw in GOL(s)
2. Plot GOL(jw) in the complex plane
3. Count encirclements of (-1,0) in the clockwise direction

## Slide 35: Nyquist Criterion
Consider the transfer function
and the P controller